## Calculator
FOR EDUCATIONAL PURPOSE ONLY – DO NOT USE THIS METHOD FOR DETAIL DESIGN – ALWAYS CONSULT A REPUTABLE SUPPLIER FOR DETAIL DESIGN
RO Membrane System Calculator
| To modify | Calculated
RO Membrane System Calculator
Warning: This calculator is for illustration purposes only. Consult a professional for detailed design.
Input Parameters - Enter values in yellow cells
| Feed Water Parameters |  |  | Value | Unit
| Feed Flow Rate |  |  | 10 | m³/h
| Feed TDS |  |  | 2000 | mg/L
| Temperature |  |  | 25 | °C
| Recovery Rate |  |  | 75 | %
| Design Flux |  |  | 20 | L/m²/h
| Safety Factor |  |  | 1.2 | -
Membrane Specifications
| Salt Rejection |  |  | 99.5 | %
Calculations
| Temperature Correction Factor (TCF) |  |  | 1
| Corrected Flux |  |  | 20 | L/m²/h
| Permeate Flow |  |  | 7.5 | m³/h
| Concentrate Flow |  |  | 2.5 | m³/h
| Required Membrane Area |  |  | 450 | m²
| Concentration Factor |  |  | 4
| Concentrate TDS |  |  | 8000 | mg/L
| Permeate TDS |  |  | 10 | mg/L
Element Calculations
| Element Area (8040) |  |  | 37.2 | m²
| Number of Elements Required |  |  | 13 | elements
| Recommended Vessels (6 elements/vessel) |  |  | 3 | vessels
| Validation Checks |  |  | Status | Limits
| Recovery Rate |  |  | OK | 50-85%
| Flux Rate |  |  | OK | 15-25 L/m²/h
| Temperature |  |  | OK | 5-45°C
| Feed TDS |  |  | OK | <45000 mg/L
Design Guidelines
| Parameter | Brackish Water | Seawater
| Typical Flux (L/m²/h) | 15-25 | 8-12
| Recovery Rate (%) | 70-85 | 35-45
| Maximum TDS (mg/L) | 15000 | 45000
If you spot a mistake or wish to suggest an improvement, please contact : contact@myengineeringtools.com
Copyright www.MyEngineeringTools.com
The content of MyEngineeringTools.com is copyrighted but no warranty nor liability is ensured. The content of this site is to be seen as a help and important information and calculation must always be double checked by the user through the quality procedure of his organization or by checking another source. The user must always respect all applicable regulation. The use of the information is at the user and its organization own risk and own cost.
FOR EDUCATIONAL PURPOSE ONLY – DO NOT USE THIS METHOD FOR DETAIL DESIGN – ALWAYS CONSULT A REPUTABLE SUPPLIER FOR DETAIL DESIGN