## Sheet1
FOR EDUCATIONAL PURPOSE ONLY – DO NOT USE THIS METHOD FOR DETAIL DESIGN – ALWAYS CONSULT A REPUTABLE SUPPLIER FOR DETAIL DESIGN
Temperature rise of centrifugal pumps at no flow and low flow
| Temperature rise at no flow |  |  |  | Temperature rise at low flow |  |  |  | Liquid temperature rise at normal flow
| Pump power at no flow | Pso | BHP | 10 | Pump head | H | ft | 180 | Power | Qshaft | kW | 9
| Weight of liquid in the pump | W1 | lb | 10 | Efficiency | eta |  | 0.3 | Efficiency | eta |  | 0.7
| Specific heat of the liquid | Cp | BTU/lb/F | 1 | Specific heat of the liquid | Cp | BTU/lb/F | 1 | Mass flowrate | m | kg/s | 12
| Temperature rise | Δtr | F/min | 42.4 | Temperature rise | Δtr | F/min | 0.53985 | Specific heat of the liquid | Cp | kJ/kg/c | 4.18
|  |  | c/min | 23.5556 |  |  | c/min | 0.29991 | Temperature rise | Δtliquid | c | 0.053828
| Pump power at no flow | Pso | kW | 7.45 | Pump head | H | m | 54.86
| Weight of liquid in the pump | W1 | kg | 4.5351 | Efficiency | eta |  | 0.3
| Specific heat of the liquid | Cp | kJ/kg/c | 4.18 | Specific heat of the liquid | Cp | kJ/kg/c | 4.18
| Temperature rise | Δtr | c/min | 23.5798 | Temperature rise | Δtr | c/min | 0.30005
If you spot a mistake or wish to suggest an improvement, please contact : contact@myengineeringtools.com
Copyright www.MyEngineeringTools.com
The content of MyEngineeringTools.com is copyrighted but no warranty nor liability is ensured. The content of this site is to be seen as a help and important information and calculation must always be double checked by the user through the quality procedure of his organization or by checking another source. The user must always respect all applicable regulation. The use of the information is at the user and its organization own risk and own cost.
FOR EDUCATIONAL PURPOSE ONLY – DO NOT USE THIS METHOD FOR DETAIL DESIGN – ALWAYS CONSULT A REPUTABLE SUPPLIER FOR DETAIL DESIGN